SEAWATER INTAKE DESIGN CALCULATOR

User Guide & Operating Manual

Gravity Intake | Pump Intake | Velocity Calculator

For Desalination Plant Marine Intake Design

# Table of Contents

1.  Overview & Purpose .............................................................. 3

2.  Opening the Software ............................................................. 3

3.  Screen Layout Explained .......................................................... 3

4.  Mode 1 — Gravity Intake Design .................................................. 4

5.  Mode 2 — Pump Intake Design ..................................................... 7

6.  Mode 3 — Velocity Calculator .................................................... 10

7.  Reading the Results ............................................................. 11

8.  Design Checks — Pass / Fail Guide ............................................... 12

9.  Sump, Surge & Maintenance Panel ................................................. 13

10. Pipe Size Selector .............................................................. 14

11. Loss Coefficients — Fitting Table ............................................... 15

12. Printing & Exporting Results .................................................... 16

13. Common Mistakes & Troubleshooting ............................................... 16

14. Glossary of Terms ............................................................... 17

# 1. Overview & Purpose

This software is a hydraulic engineering calculator designed to help engineers design seawater intake systems for desalination plants. It does not require any programming knowledge — all inputs are typed into fields and results are calculated automatically.

The calculator covers three design scenarios:

- Gravity Intake — seawater flows by gravity from the sea through a buried pipe to a sump tank at the plant, with no pumps in the intake line.

- Pump Intake — submersible or dewatering pumps draw seawater from the sea and push it to the plant through a pressurized pipeline.

- Velocity Calculator — a standalone tool to quickly check flow velocity, head loss, and Reynolds number for any pipe and flow combination.

This tool is based on internationally recognized hydraulic equations: Darcy-Weisbach friction loss, Swamee-Jain friction factor, Joukowsky surge equations, and ANSI/HI pump standards. Pipe dimensions follow ISO 4427 / EN 12201 for HDPE PE100.

# 2. Opening the Software

Step 1: Locate the file

Find the file named intake_calc.html on your computer. It is a single file — there are no other files needed.

Step 2: Open in browser

Double-click the file. It will open automatically in your web browser (Chrome, Edge, Firefox, or Safari). No internet connection is required.

Step 3: Do not move or rename

The file is self-contained. You may copy it, but do not rename it or move it without its companion files if any exist.

⚠ Do not open this file inside a company intranet document viewer or SharePoint preview. Always open it directly in a browser for full functionality.

# 3. Screen Layout Explained

The screen is divided into two main zones:

| Zone | Description |
| --- | --- |
| LEFT PANEL (30%) | All input fields. This is where you enter your project data. Organized into collapsible sections. Click any section header to expand or collapse it. |
| RIGHT PANEL (70%) | All results and charts. Updates automatically every time you change any input. Contains: Hydraulic Results, Design Checks, Sump/Surge/Maintenance panel, and graphs. |
| TOP TABS | Three tabs at the top switch between: Gravity Intake, Pump Intake, and Velocity Calc. Each tab has its own set of inputs and outputs. |

# 4.  Mode 1 — Gravity Intake Design

Use this mode when seawater flows naturally from the sea to the plant with no pumps — driven purely by the difference in water level between the sea surface and the sump tank.

## 4.1 How Gravity Intake Works

The sea level is always higher than the sump water level at the plant. This height difference (called available head) pushes water through the buried HDPE pipe. The calculator verifies that this available head is sufficient to overcome friction in the pipe and losses through fittings and screens.

The most critical condition is at Lowest Astronomical Tide (LAT). At this moment, the sea is at its lowest, so available head is at its minimum. The design must work at LAT — if it works then, it will work at all other times.

## 4.2 Input Fields — Gravity Mode

Fill in all fields in the left panel. All have engineering defaults pre-loaded from the project basis. Change only what differs from your site conditions.

Section: Flow & Pipe

| Field Name | What to Enter / What It Means |
| --- | --- |
| Max Design Flow | The maximum flow the intake must deliver — in m³/hr. This is the design capacity of the desalination plant intake. |
| Min Acceptable Flow | The lowest flow the system must still deliver under worst conditions (e.g., single-pipe operation). In m³/hr. |
| Total Pipe Length | The total length of the HDPE pipe from the offshore intake head to the sump tank. Include both the offshore and onshore sections. In meters. |
| Seawater Temperature | Average operating seawater temperature at the site in °C. Affects viscosity and density used in calculations. Typical range: 20–35°C for Gulf/Oman. |
| Pipe Roughness ε | Surface roughness of the pipe inner wall. For new HDPE PE100, use 0.0015 mm. Do not change unless using a different pipe material. |
| Number of Parallel Pipes | How many pipes run in parallel between sea and sump. Enter 2 for dual-pipe redundancy (recommended). Each pipe carries half the total flow. |
| Diameter Selection Mode | Choose Auto to let the calculator find the optimal pipe size, or Manual to select a specific DN from the dropdown list. |
| Nominal Pipe Diameter | Visible only in Manual mode. Select the HDPE DN size you wish to evaluate. The calculator will show results for that size even if it fails checks. |
| Pipe Pressure Class (SDR) | Select the SDR rating of the HDPE pipe. SDR17 (PN10) is standard for gravity intakes. Higher pressure pipes (lower SDR) have thicker walls and smaller bore. |

Section: Levels & Site

| Field Name | What to Enter / What It Means |
| --- | --- |
| Lowest Tide Level — LAT | The Lowest Astronomical Tide elevation at your site, relative to the local tide datum. Enter as a negative number if below datum. Example: −0.3 m means 0.3 m below datum. |
| Highest Tide Level — HAT | The Highest Astronomical Tide. Enter as a positive number above datum. Used to check that no reverse flow occurs when tide is high. |
| Seabed Depth at Intake | The depth of the seabed at the offshore intake location, measured below tide datum. Enter as a negative value. Example: −4.5 m. |
| Sump Operating Water Level | The water surface level inside the sump tank during normal operation, relative to tide datum. Enter as a negative value (sump is below sea level). Example: −1.5 m. |

Section: Loss Coefficients — Fitting Table

See Section 11 of this guide for full instructions on how to use the fitting table.

## 4.3 What the Calculator Does

After you enter your inputs, the calculator automatically:

- Computers the available gravity head at LAT and HAT

- Iterates pipe diameters from DN200 to DN1200 to find the smallest size where all checks pass (Auto mode)

- Calculates friction loss using Darcy-Weisbach equation with Swamee-Jain friction factor

- Sums all fitting losses from your fitting table

- Checks velocity at maximum flow and minimum single-pipe flow

- Verifies intake submergence to prevent vortex formation

- Calculates sump tank dimensions, surge wave speed, and minimum valve closing time

## 4.4 Key Rules for Gravity Design

| Check | Pass (Green) | Action if Fail (Red) |
| --- | --- | --- |
| Head Margin > 0.2 m | ✓ Enough gravity head to overcome all losses with 0.2 m safety margin | ✗ Lower sump level, reduce pipe length, increase pipe diameter, or reduce fittings |
| Velocity 0.8–2.0 m/s at Qmax | ✓ Flow is fast enough to prevent sediment and slow enough to avoid excess loss | ✗ Adjust pipe diameter — too slow: reduce DN; too fast: increase DN |
| Velocity ≥ 0.6 m/s at Qmin | ✓ Single-pipe emergency flow still prevents sediment deposition | ✗ Increase pipe roughness or use velocity-control valve |
| Submergence ≥ S_min | ✓ Intake head is deep enough to prevent air vortex entering the pipe | ✗ Lower the pipe invert depth or relocate intake further offshore |
| Screen slot ≤ 0.15 m/s | ✓ Slot velocity protects marine life and reduces biofouling | ✗ Increase screen area or use larger wedge-wire screen |
| No reverse pressure at HAT | ✓ No reverse flow when tide is at highest | ✗ Usually passes automatically if sump level is set correctly |

# 5.  Mode 2 — Pump Intake Design

Use this mode when pumps are used to lift seawater from the sea to the plant. This is appropriate when the plant elevation is significantly above sea level or when gravity head is insufficient.

## 5.1 How Pump Intake Works

One or more duty pumps (submersible or dewatering type) draw water from the sea and push it through a pressurized HDPE pipeline to the plant. The calculator finds the operating point where the pump curve intersects the system resistance curve, confirming actual delivered flow and head.

Parallel pumps are used in this calculator — each pump operates at the same head, and their flows add together. Adding more duty pumps increases total flow but each pump delivers less flow than its rated point.

## 5.2 Pump Types Explained

| Field Name | What to Enter / What It Means |
| --- | --- |
| Submersible Pump | The pump motor and impeller are installed underwater, below the sea surface. Water is pushed up to the plant. NPSH is always satisfied because the pump is submerged. Best for permanent installations. |
| Dewatering Pump | Surface-mounted pump that sucks water up from below using suction lift. Limited by the physical maximum suction lift (approximately 6.5–7.0 m at sea level). Best for temporary or emergency installations. |

⚠ Dewatering pumps must never be used if the required suction lift exceeds the maximum suction lift shown in the results. The calculator will display a red warning if this limit is exceeded.

## 5.3 Input Fields — Pump Mode

Section: Flow & Pipe (shared with Gravity mode)

Same fields as Gravity mode. Refer to Section 4.2 above. Note: SDR11 (PN16) is recommended as default for pump discharge pipes.

Section: Levels & Site (shared with Gravity mode)

Same LAT, HAT, and seabed fields. The sump level field is not used in pump mode — replaced by the plant inlet elevation below.

Section: Pump System

| Field Name | What to Enter / What It Means |
| --- | --- |
| Plant Inlet Elevation | The elevation at which the pipe delivers water to the plant, measured in meters above the LAT datum. This is the static head the pump must overcome as a minimum. Example: 10 m means the plant inlet is 10 m above lowest tide. |
| Pump Installation Type | Select Submersible or Dewatering. This changes which NPSH formula is used and enables the suction lift warning for dewatering pumps. |
| Number of Duty Pumps | How many pumps run simultaneously during normal operation. Enter 1, 2, 3, etc. Total flow = flow per pump × number of duty pumps. |
| Number of Standby Pumps | How many spare pumps are installed but not running. Standby pumps start automatically if a duty pump fails. Recommended minimum: 1 standby. |

Section: Pump Curve & Power

| Field Name | What to Enter / What It Means |
| --- | --- |
| Shutoff Head H₀ (m) | The head produced by the pump at zero flow — read from the top-left of the pump curve on the manufacturer datasheet. Always higher than rated head. |
| Rated Head Hr (m) | The head at the pump's rated (best efficiency) operating point. Read from the pump datasheet. Enter the value at the Best Efficiency Point (BEP). |
| Rated Flow per Pump (m³/hr) | The flow at the pump's rated (best efficiency) operating point. Read from the pump datasheet. This defines the shape of the pump curve in the calculator. |
| Pump Efficiency η (0–1) | Hydraulic efficiency of the pump at its operating point. Expressed as a decimal: 0.72 means 72%. Read from pump datasheet efficiency curve at the operating point. |
| Motor Efficiency η (0–1) | Electrical efficiency of the motor driving the pump. Expressed as a decimal: 0.92 means 92%. Typically, 0.88 to 0.95 for modern motors. |

Section: NPSH & Geometry

| Field Name | What to Enter / What It Means |
| --- | --- |
| NPSH Required — from datasheet (m) | The Net Positive Suction Head required by the pump, stated by the manufacturer on the pump datasheet. The actual NPSH available at site must always exceed this value by at least 0.5 m. |
| Pump Depth Below LAT (m) | Submersible pumps only. How far below the Lowest Astronomical Tide the pump impeller is installed. A larger submergence improves NPSH and reduces vortex risk. Minimum recommended: 1.5 m. |
| Suction Lift Height (m) | Dewatering pumps only. The vertical height from the water surface to the pump suction inlet. Must be less than the maximum suction lift shown in results (typically 6.5 m). |

## 5.4 Understanding the Pump Curve Chart

The pump curve chart shows four lines:

- System Curve at LAT (solid line) — the resistance the system presents to the pump at the lowest tide. This is the worst case (highest static head).

- System Curve at HAT (dashed line) — resistance at highest tide. Lower static head means the pump delivers more flow at high tide.

- Single Pump Curve — head-flow relationship for one pump alone.

- Combined Pump Curve (n duty pumps) — flows from all duty pumps added horizontally. The actual operating point is where this line crosses the system curve at LAT.

The red dot on the chart is the operating point — the actual flow and head delivered. The calculator reads this point and uses it for all power, NPSH, and velocity calculations.

# 6.  Mode 3 — Velocity Calculator

A standalone quick-check tool. Use it independently of any project to verify velocity, head loss, or required pipe size for any pipe and flow combination.

## 6.1 Selecting a Calculation Mode

Use the dropdown at the top of the Velocity Calc tab to choose what you want to calculate:

| Field Name | What to Enter / What It Means |
| --- | --- |
| Flow + Diameter → Velocity | You know the flow rate and pipe size. The calculator tells you the velocity and whether it is acceptable. |
| Velocity + Diameter → Flow | You know the maximum velocity you want and the pipe size. The calculator tells you the maximum flow you can pass. |
| Velocity + Flow → Diameter | You know the flow rate and maximum velocity allowed. The calculator recommends the minimum pipe diameter required. |

## 6.2 Velocity Zone Badges

| Badge Colour | Velocity Range | Meaning & Action |
| --- | --- | --- |
| 🔴 Red | < 0.6 m/s | Too slow — sediment will settle in the pipe over time. Increase flow or reduce pipe diameter. |
| 🟠 Amber | 0.6 – 0.8 m/s | Marginal — acceptable for short durations but not ideal for continuous operation. Monitor for sediment build-up. |
| 🟢 Green | 0.8 – 2.0 m/s | Optimal for gravity intake pipelines. Flow is fast enough to prevent sediment and slow enough to keep head loss manageable. |
| 🟢 Green | 1.5 – 2.5 m/s | Optimal for pumped intake pipelines. Higher velocity is acceptable because pump head is available. |
| 🔴 Red | > 2.5 m/s | Too fast — excessive head loss, risk of pipe erosion and water hammer. Increase pipe diameter. |

# 7. Reading the Results

All results appear in the right panel and update instantly. Results are organised into three groups:

## 7.1 Flow & Velocity Group

| Field Name | What to Enter / What It Means |
| --- | --- |
| Operating Flow | Total flow actually delivered by the system at the calculated operating point. Compare to Max Design Flow and Min Acceptable Flow. |
| Flow per Pipe | Flow carried by each individual parallel pipe. Used to verify velocity in each pipe. |
| Flow Velocity | Actual velocity inside the pipe at maximum design flow. Must be within the green zone for your intake type. |
| Reynolds Number | Indicates whether flow is turbulent (>4000 — normal for these velocities), transitional (2300–4000), or laminar (<2300 — should not occur in intake design). |
| Darcy Friction Factor | Calculated friction factor used in head loss equation. Shown for reference — no action needed unless debugging. |

## 7.2 Head Budget Group

| Field Name | What to Enter / What It Means |
| --- | --- |
| Available Gravity Head | Total head available to drive flow, from sea surface to sump level at LAT. This is the energy budget. |
| Friction Head Loss | Head consumed by pipe wall friction over the full pipe length. Largest component of total head loss. |
| Minor (Fitting) Losses | Head consumed by all fittings combined — screens, valves, elbows, entrance, exit. Driven by your fitting table entries. |
| Available Head Margin | Remaining head after subtracting all losses from available head. Must be > 0.2 m (green) for a valid gravity design. A larger margin means a more robust design. |
| Total Dynamic Head | Pump mode only. Total head the pump must produce — sum of static lift plus all friction and fitting losses. |

## 7.3 Pipe Geometry Group

| Field Name | What to Enter / What It Means |
| --- | --- |
| Selected Pipe Size | The recommended or selected HDPE DN size. In Auto mode this is the smallest passing size. In Manual mode this reflects your selection. |
| Pipe Outer Diameter | External diameter of the selected HDPE pipe. Used for trench width and burial depth calculations. |
| Pipe Inner Diameter | Internal diameter — the bore through which water flows. Determined by DN and SDR selection. |
| Wall Thickness | Pipe wall thickness. Determines pressure rating. Calculated as OD ÷ SDR. |
| Pipe Invert Depth | Depth of the bottom of the pipe below LAT at the intake end. Must be deep enough to ensure adequate cover above the seabed. |

8.  Design Checks — Pass / Fail Guide

The Design Compliance Checks section shows a summary banner at the top (green = all pass, red = number of failures) and individual check rows below. Each row shows the check name, a brief explanation, and a color-coded badge.

## 8.1 What to Do When a Check Fails

| Field Name | What to Enter / What It Means |
| --- | --- |
| Head Margin < 0.2 m | Lower the sump water level (make z_sump more negative), increase pipe diameter, or reduce the number or severity of fittings in the fitting table. |
| Velocity too low (< 0.8 m/s) | Reduce pipe diameter by one DN step in Manual mode or let Auto mode select a smaller pipe. |
| Velocity too high (> 2.0 m/s gravity or > 2.5 m/s pump) | Increase pipe diameter by one DN step or increase number of parallel pipes. |
| Submergence insufficient | Lower the pipe invert by increasing the burial depth or relocate the intake further offshore where the seabed is deeper. |
| Screen slot velocity > 0.15 m/s | The wedge-wire screen area is too small for the flow. Request a larger screen area from the supplier. |
| NPSH margin < 0.5 m | Increase pump submergence depth, reduce suction pipe losses, or select a pump with lower NPSH required. |
| Suction lift exceeds maximum | Dewatering pump cannot physically lift water from this depth. Switch to submersible pump type. |
| Operating flow outside range | Pump curve and system curve do not intersect in a usable region. Adjust pump rated point (H₀, Hr, Qr) to match the system. |

9. Sump Tank, Surge & Maintenance Panel

This panel is at the bottom of the right panel and contains three sub-sections, each with a distinct background colour.

## 🏊 Sump Tank

The sump tank is the receiving chamber at the plant where seawater arrives before entering the desalination process. The calculator sizes the sump based on 3 minutes of retention time at maximum flow.

| Field Name | What to Enter / What It Means |
| --- | --- |
| Sump Volume (m³) | Minimum required internal volume. Sized to allow pump cycling, debris settling, and surge absorption. Increase retention time by editing the code if more buffer is needed. |
| Length (m) | Recommended sump length based on hydraulic institute pump sump geometry rules. Provides adequate pump suction conditions. |
| Width (m) | Minimum width — at least twice the pump bell diameter to prevent vortex formation near pump suction. |
| Depth (m) | Total sump depth from operating water level to floor, including pump submergence clearance. |

## ⚡ Surge

Water hammer (surge) occurs when flow is suddenly stopped — typically when a valve closes quickly. HDPE pipe naturally dampens surge far better than steel, but valves must still close slowly.

| Field Name | What to Enter / What It Means |
| --- | --- |
| Surge Wave Speed (m/s) | Speed at which a pressure wave travels through the water in the HDPE pipe. Lower for HDPE than steel — this is a benefit of HDPE. |
| Maximum Surge Head (m) | The worst-case pressure spike if flow is stopped instantaneously. This is a theoretical maximum — slow valve closing eliminates most of this. |
| Min. Valve Closing Time (s) | The minimum time a valve must take to fully close to avoid damaging water hammer. Always specify slow-closing (motorized) valves for isolation on this line. |

## 🔧 Maintenance Checklist

This section provides operating and maintenance guidance. These are not calculated values — they are standard recommendations for seawater intake systems:

- Chlorination: Inject 0.2–0.5 mg/L continuously, or 1–2 mg/L shock dose for 1 hour per day, at the offshore intake head to prevent marine biofouling inside the pipe.

- Pigging: Schedule pipe cleaning runs at 1.0–3.0 m/s using foam pigs at the frequency determined during commissioning (typically every 3–12 months).

- Air valves: Install combination air release/vacuum break valves at all local high points along the pipeline route.

- Inspection: Manholes for inspection and access should be provided every 100 m maximum on the onshore section.

# 10. Pipe Size Selector

The pipe size selector is at the top of the Flow & Pipe section in both Gravity and Pump modes.

## 10.1 Auto Mode

The calculator tests every standard HDPE DN size from DN200 to DN1200 and selects the smallest size that passes all design checks. This is the recommended mode for initial design.

## 10.2 Manual Mode

Select Manual from the Diameter Selection Mode toggle and choose a specific DN from the dropdown list. The calculator evaluates that specific size and reports pass/fail for all checks. Use this to:

- Verify a specific pipe size that is already procured or specified

- Compare different sizes side by side (change the selection and note results)

- Check whether a standard locally available size works for your design

⚠ In Manual mode, the calculator will not prevent you from selecting a pipe that fails checks. It will show red badges on failing checks. You must review and act on failures yourself.

## 10.3 SDR Selection

The SDR dropdown changes the pipe wall thickness and internal diameter for the selected DN. This affects velocity (thicker wall = smaller bore = higher velocity) and pressure rating.

| Field Name | What to Enter / What It Means |
| --- | --- |
| SDR 17 — PN10 | Standard for gravity intake pipes. Sufficient pressure rating for this application. Largest bore for a given DN. |
| SDR 13.6 — PN12.5 | Intermediate rating. Use for low-pressure pumped lines up to 5 bar working pressure. |
| SDR 11 — PN16 | Recommended for pump discharge pipes. Thicker wall handles higher pressures from pumps. |
| SDR 7.4 — PN25 | Heavy duty. Use only if system pressure exceeds 16 bar — uncommon for intake applications. |

# 11.  Loss Coefficients — Fitting Table

The fitting table in the Loss Coefficients section replaces manual K-value entry with a structured table that accounts for every fitting in the pipeline.

## 11.1 How to Use the Fitting Table

Step 1: Review pre-loaded fittings

The table comes pre-loaded with all common fitting types and their standard K values. The Screen (50% fouled) and Pipe Exit rows are locked — they are always present in the design.

Step 2: Enter quantities

In the No. of Fittings column, type the number of each fitting type present in your pipeline. Type 0 for fittings not present. The K × Qty column updates automatically.

Step 3: Modify K values if needed

The Loss Coeff. K values can be edited if your fitting supplier provides different values. For standard fittings, do not change the defaults.

Step 4: Add custom fittings

Click + Add Custom Fitting to add a row for any fitting not in the default list. Enter its name, K value, and quantity.

Step 5: Check total ΣK

The Total ΣK at the bottom of the table shows the sum of all fitting losses. This value is used directly in the head loss calculation. A high ΣK means significant fitting losses — check that your design has sufficient head margin.

## 11.2 Common K Values Reference

| Field Name | What to Enter / What It Means |
| --- | --- |
| Intake bellmouth entrance | K = 0.05 — a well-rounded entrance. If using a sharp-edged pipe entrance, use K = 0.5 instead. |
| Wedge-wire screen (clean) | K = 0.5 — new, clean screen with no fouling. |
| Wedge-wire screen (50% fouled) | K = 2.5 — locked at this value to ensure the design accounts for partially blocked screen conditions. |
| 90° long radius elbow | K = 0.30 — standard long radius bend. Count each bend in the pipeline individually. |
| Gate valve (full open) | K = 0.15 — isolation valve fully open. Do not use partial-open K values for design — valves should always be fully open or fully closed in this application. |
| Pipe exit to sump | K = 1.0 — fixed loss where pipe discharges into the sump tank. Always 1 fitting. |

# 12. Printing & Exporting Results

Click the Print button at the top right of the screen to generate a printable version of the current calculation state. The print view is formatted as a clean A4 report showing:

- All input values used in the calculation

- All hydraulic output results

- Design check summary with pass/fail status

- Sump, surge, and maintenance data

Use your browser's Print to PDF function to save the output as a PDF file. In Chrome or Edge: File → Print → Destination: Save as PDF.

# 13. Common Mistakes & Troubleshooting

| Problem | Solution |
| --- | --- |
| All results show 0 or NaN | One or more required input fields are empty or contain invalid text. Check that all numerical fields contain numbers, not letters or blank. |
| Head margin is negative | The gravity head is insufficient to push the required flow. Lower the sump level (more negative z_sump), increase pipe diameter, or reduce fitting quantities. |
| Velocity is far too high | You may have entered flow in m³/s instead of m³/hr. Check units — all flow fields require m³/hr. |
| Pump operating point not found | The pump curve and system curve do not intersect. Check that H₀ > TDH_static. If H₀ is too low, the pump cannot overcome static head. |
| Suction lift warning appears | The dewatering pump cannot lift water from the entered depth. Either reduce the suction lift, or switch to Submersible pump type. |
| Checks pass but velocity is amber | Amber (marginal) means the velocity is between 0.6 and 0.8 m/s — acceptable but not ideal. Consider reducing pipe diameter by one DN step. |
| Screen slot velocity fails | More screen area is needed. The wedge-wire screen on site may need to be replaced with a larger unit, or a second screen installed in parallel. |
| Section content not visible | Click the section header to expand it. All sections are collapsible — they may have been collapsed accidentally. |

# 14. Glossary of Terms

| Field Name | What to Enter / What It Means |
| --- | --- |
| LAT | Lowest Astronomical Tide — the lowest predicted tidal level under average meteorological conditions. The critical design condition for gravity intake. |
| HAT | Highest Astronomical Tide — the highest predicted tidal level. Used to check reverse pressure and high-tide pump conditions. |
| Datum | A reference elevation (zero point) from which all levels are measured. All elevations in this calculator are relative to the local tide datum. |
| TDH | Total Dynamic Head — the total head a pump must generate, including static lift, friction, and fitting losses. |
| NPSH | Net Positive Suction Head — the minimum pressure that must exist at the pump suction to prevent cavitation (vapor bubble formation that damages the pump). |
| Darcy-Weisbach | The standard equation for calculating friction head loss in pipes: hf = f × (L/D) × V²/(2g). |
| SDR | Standard Dimension Ratio — the ratio of pipe outer diameter to wall thickness. Lower SDR = thicker wall = higher pressure rating. |
| Reynolds Number (Re) | A dimensionless number indicating flow regime. Re > 4000 means turbulent flow, which is the normal condition for water intake pipelines. |
| Friction Factor (f) | The Darcy friction factor — a measure of pipe wall resistance to flow. Calculated using Swamee-Jain equation in this software. |
| Submergence | The depth of water above the pipe intake bell or pump impeller. Sufficient submergence prevents air vortex formation. |
| Water Hammer / Surge | A pressure spike caused by sudden change in flow velocity. Occurs when valves close quickly. HDPE pipes are naturally resistant, but slow valve closure is still required. |
| Biofouling | Growth of marine organisms (algae, barnacles, mussels) inside the pipe. Controlled by chlorination and periodic pigging. |
| Pigging | A pipe cleaning process where a foam or solid plug (pig) is pushed through the pipe by water pressure to remove biological growth and sediment deposits. |
| Head Loss | Energy lost to friction and turbulence as water moves through pipes and fittings. Expressed in meters of water column. |
| PN Rating | Pressure Nominal — the maximum continuous working pressure of the pipe at 20°C, in bar. PN10 = 10 bar maximum for PE100 SDR17. |

End of User Guide

Seawater Intake Design Calculator • Based on ISO 4427, EN 12201, Darcy-Weisbach, ANSI/HI 9.8